Here’s a fully structured, operations-ready Preventative Maintenance Schedule and a Baseline Performance Sheet tailored for a water-facility with ~100 identical pumps. I’ve built these so you can drop them straight into your CMMS, SharePoint, or technician workflow.

Preventative Maintenance Schedule (PMS)

Purpose: Maintain reliability, reduce outages, and ensure consistent pump performance across the entire fleet.

🟦 Daily Checks (Operator Level)

- Visual inspection of pump, motor, and surrounding area

- Check for leaks around seals, flanges, and valves

- Listen for abnormal noise (grinding, cavitation, rattling)

- Verify discharge pressure is within normal operating range

- Confirm suction source (wet well, tank, intake) is clear and at correct level

- Check control panel indicators (run status, alarms, alternation)

🟩 Weekly Checks (Technician Level)

- Record flow rate & pressure readings for trending

- Check vibration levels (handheld meter or feel test)

- Inspect electrical connections for heat, looseness, corrosion

- Clean suction screens / wet well debris

- Check pump run hours and compare against expected duty cycle

- Verify float switches / level sensors are functioning and not fouled

🟧 Monthly Checks (Maintenance Team)

- Inspect mechanical seals for wear or minor leakage

- Check bearing temperature (IR thermometer or thermal camera)

- Measure motor amp draw and compare to baseline

- Inspect impeller condition (if accessible)

- Check alignment between pump and motor

- Lubricate bearings (if applicable)

- Test emergency stop and interlocks

🟥 Quarterly Checks (Engineering / Reliability Team)

- Full vibration analysis (ISO 10816 or site standard)

- Thermal imaging of motor, bearings, and electrical cabinet

- Check insulation resistance of motor windings

- Inspect non-return valves for wear or sticking

- Verify pump efficiency using flow, pressure, and power draw

- Update performance trend charts for all pumps

⬛ Annual Checks (Major Service)

- Remove pump for full inspection (if duty allows)

- Inspect and clean impeller, volute, wear rings

- Replace mechanical seals (if condition warrants)

- Replace bearings (if condition warrants)

- Repaint / corrosion protection

- Motor service (bearing check, cleaning, insulation test)

- Update baseline performance sheet with new benchmark values

- Review failure history and adjust PMS intervals

Baseline Performance Sheet (Template)

This is the sheet you use to establish the “healthy” operating profile for each pump. Every future reading is compared against this baseline to detect early degradation.

Pump Baseline Performance Sheet – Template

Pump ID: Location: Duty / Standby: Manufacturer / Model: Installation Date: Last Major Service:

1. Hydraulic Performance

- Design Flow Rate:

- Baseline Flow Rate (commissioning):

- Design Discharge Pressure:

- Baseline Discharge Pressure:

- Suction Pressure (if applicable):

- Pump Efficiency (%):

2. Electrical Performance

- Rated Motor Power (kW):

- Rated Voltage:

- Rated Current:

- Baseline Running Current (Amps):

- Baseline Power Factor:

- Baseline Motor Temperature:

3. Mechanical Condition

- Baseline Vibration (mm/s RMS):

  - Axial:

  - Horizontal:

  - Vertical:

- Baseline Bearing Temperature:

- Baseline Seal Condition:

- Alignment Status:

4. Environmental / Installation Factors

- Wet well condition at commissioning:

- Suction pipe condition:

- Check valve condition:

- Isolation valve condition:

- Electrical cabinet condition:

5. Control & Automation

- Start/Stop method:

- Alternation logic:

- Alarm setpoints:

- Trip setpoints:

- Run hours at baseline:

6. Notes & Photos

- Commissioning photos

- Motor nameplate photo

- Pump nameplate photo

- Any installation anomalies

If you want, I can also build:

- A fleet-wide master sheet for all 100 pumps

- A trend analysis dashboard (flow, pressure, amps, vibration)

- A risk-based maintenance plan (RBI)

- A criticality ranking for your pump fleet

- A technician-friendly checklist formatted for mobile devices

Just tell me how deep you want to go and whether you want this in table form, CSV-ready, or formatted for your CMMS.